## Word Mapping
Data Protocol Mapping for ESEPRO LS 4 Emulation using LS-5 Data Protocol 5302
Version 2, 8/7/2024
No. | Profibus | LS 4 Content | LS 4 Unit | LS-5 Mux | Start | Parameter ID | Type | LS-5 Description | LS5 Unit | Conversion Operation | Comment
1 | 10 | Protocol number "1600" |  | 0 | 0 | - | int16 | n/a | - | Emulated
2 | 12 | Voltage L12, system [A] | V × 10UGNEXPO | 8 | 25 | 108 | int32 | System A voltage L1-L2 | 0.1 V | divide by 10
3 | 14 | Voltage L23, system [A] | V × 10UGNEXPO | 10 | 31 | 109 | int32 | System A voltage L2-L3 | 0.1 V | divide by 10
4 | 16 | Voltage L31, system [A] | V × 10UGNEXPO | 12 | 37 | 110 | int32 | System A voltage L3-L1 | 0.1 V | divide by 10
5 | 18 | Voltage L1N, system [A] | V × 10UGNEXPO | 9 | 28 | 114 | int32 | System A voltage L1-N | 0.1 V | divide by 10
6 | 20 | Voltage L2N, system [A] | V × 10UGNEXPO | 11 | 34 | 115 | int32 | System A voltage L2-N | 0.1 V | divide by 10
7 | 22 | Voltage L3N, system [A] | V × 10UGNEXPO | 13 | 40 | 116 | int32 | System A voltage L3-N | 0.1 V | divide by 10
8 | 24 | Frequency, system [A] | Hz × 100 | 2 | 6 | 144 | int16 | System A frequency | 0.01 Hz | 1:1
9 | 26 | Current in L1, system [A] | A × 10IGNEXPO | 5 | 16 | 111 | int32 | System A current 1 | 0.001 A | divide by 1000
10 | 28 | Current in L2, system [A] | A × 10IGNEXPO | 6 | 19 | 112 | int32 | System A current 2 | 0.001 A | divide by 1000
11 | 30 | Current in L3, system [A] | A × 10IGNEXPO | 7 | 22 | 113 | int32 | System A current 3 | 0.001 A | divide by 1000
12 | 32 | Power factor cos ϕ dimensionless |  | 1 | 3 | 160 | int16 | System A power factor (cos.phi) | 0.001 | divide by 10
13 | 34 | Real power P, system [A] | W × 10PGNEXPO | 3 | 10 | 337 | int32 | System A total active power | 1 W | divide by 1000
14 | 36 | Re-active power Q, system [A] | var × 10PNTEXPO | 0 | 1 | 136 | int32 | System A total reactive power | 1 var | divide by 1000
15 | 38 | Voltage L12, system [B] | V × 10UGNEXPO | 21 | 64 | 118 | int32 | System B voltage L1-L2 | 0.1 V | divide by 10
16 | 40 | Voltage L23, system [B] | V × 10UGNEXPO | 23 | 70 | 119 | int32 | System B voltage L2-L3 | 0.1 V | divide by 10
17 | 42 | Voltage L31, system [B] | V × 10UGNEXPO | 25 | 76 | 120 | int32 | System B voltage L3-L1 | 0.1 V | divide by 10
18 | 44 | Frequency, system [B | Hz × 100 | 16 | 48 | 147 | int16 | System B frequency | 0.01 Hz | 1:1
19 | 46 | Exponents UGNEXPO [A] IGNEXPO |  | - |  | - | - | n/a | - | set to 0 for V and A
20 | 48 | Exponents: PGNEXPO, UNTEXPO [B] |  | - |  | - | - | n/a | - | set to 3 for kW, set to 0 for V
21 | 50 | Internal alarms 1 | register |  |  |  | uint16 | Refer to Register Bits mapping sheet | - | map bits
22 | 52 | Internal alarms 2 | register |  |  |  | uint16 | Refer to Register Bits mapping sheet | - | map bits
23 | 54 | Internal alarms 3 | register |  |  |  | uint16 |  | - | set to 0 | Internal, not supported
24 | 56 | Internal alarms 4 | register |  |  |  | uint16 |  | - | set to 0 | Internal, not supported
25 | 58 | Internal alarms 5 | register |  |  |  | uint16 |  | - | set to 0 | Internal, not supported
26 | 60 | Internal alarms 6 | register |  |  |  | uint16 |  | - | set to 0 | Internal, not supported
27 | 62 | Internal alarms 7 | register |  |  |  | uint16 |  | - | set to 0 | Internal, not supported
28 | 64 | Internal Diagnosis | register |  |  |  | uint16 |  | - | set to 0 | Internal, not supported

## Register Bits mapping
Register Bits Mapping for ESEPRO GW-4 to LS 4 Emulation using LS-5
Version 2, 8/7/2024
LS 4 Register Name | Mux No. | LS-5 Register Name | Comment
Internal alarm 1
Overfrequency level 2 | 29 | 07.07 System A overfrequency threshold 2
Underfrequency level 2 | 29 | 07.09 System A underfrequency threshold 2
Overvoltage level 2 | 29 | 07.11 System A overvoltage threshold 2
Undervoltage level 2 | 29 | 07.13 System A undervoltage threshold 2
Internal alarm 2
Overfrequency level 1 | 29 | 07.06 System A overfrequency threshold 1
Underfrequency level 1 | 29 | 07.12 System A undervoltage threshold 1
Overvoltage level 1 | 29 | 07.10 System A overvoltage threshold 1
Undervoltage level 1 | 29 | 07.12 System A undervoltage threshold 1
df/dt alarm | 30 | 07.15 df/dt (ROCOF)
Asymmetry | 29 | 07.26 System A voltage asymmetry (with negative sequence)
dϕ/dt phase/vector jump | 29 | 07.14 System A phase shift
Internal alarm 7
Wrong rotary field | 9 | 00.04 LM Internal flag 5 | Use LogicManager
Internal Diagnosis
terminal 32 | 9 | 00.01 LM Internal flag 1 | Use LogicManager
terminal 31 | 9 | 00.02 LM Internal flag 2 | Use LogicManager
terminal 74 | 9 | 00.03 LM Internal flag 3 | Use LogicManager
terminal 75 | 9 | 00.04 LM Internal flag 4 | Use LogicManager